Below is a direct, model-engineering–level answer to both parts of your question. I’ll be explicit about what is missing, why it is missing, and what must change for positive-sequence dynamics to be usable in RMS Dynamic Phasor (DP) simulations.

1. What Additional Data Is Required for DP That Is Not in Positive-Sequence Programs?

Positive-sequence RMS programs intentionally collapse three-phase physics into a single balanced channel. DP relaxes that assumption. As a result, DP requires new degrees of freedom, not just more detail.

A. Network Data: From “+Seq Only” → Sequence-Coupled or Phase Models

✅ Already in +Seq RMS

- Z1,Y1

- Balanced shunts

- Balanced transformer leakage

- Balanced topology

❌ Missing for DP

You must add at least one of the following:

Option 1 – Sequence-Domain DP (most common)

- Negative-sequence impedance Z2and admittance Y2

- Zero-sequence impedance Z0and admittance Y0

- Explicit ground return assumptions

- Zero-sequence blocking or circulation paths

Option 2 – Phase-Domain DP

- Full phase impedance and admittance matrices Zabc,Yabc

- Mutual coupling

- Transposition / asymmetry data

Key point:
Positive-sequence programs do not store enough information to reconstruct Z2, Z0, or phase coupling unless it was separately entered.

B. Transformers: Zero-Sequence Physics (Usually Lost in +Seq)

❌ Missing for DP

- Vector group (Yg-Δ, Δ-Yg, zig-zag, etc.)

- Neutral grounding impedance

- Zero-sequence leakage paths

- Delta circulating current dynamics

In +seq RMS, a transformer is often just a scalar impedance. In DP, it is a topological sequence filter.

C. Loads: Phase and Sequence Resolution

✅ In +Seq RMS

- Balanced PQ or ZIP

- One control state

❌ Required for DP

- Per-phase load distribution

- Connection type (wye grounded, wye ungrounded, delta)

- Sequence-specific voltage sensitivity (ZIP per phase or per sequence)

- Single-phase / two-phase load identification

Without this, DP cannot initialize a physically meaningful unbalanced steady state.

D. Sources and Grid Equivalents

❌ Missing for DP

- Z2, Z0of the grid Thevenin equivalent

- Grounding impedance of the source

- Negative-sequence damping assumptions

Positive-sequence short-circuit data alone is not sufficient.

E. Machines (Synchronous, Induction, Motors)

✅ In +Seq RMS

- Swing equation

- Xd,Xq,Xd'

- Exciter and governor

❌ Required for DP

- Negative-sequence reactance X2

- Zero-sequence reactance X0

- Negative-sequence torque / heating representation

- Grounding of stator neutral

Without this, DP cannot simulate torque oscillations driven by unbalanced currents.

F. Inverter-Based Resources (Largest Gap)

This is where +seq RMS is fundamentally incompatible with DP.

✅ In +Seq RMS

- dq control around positive-sequence voltage

- Single PLL

- Balanced current injection

- Scalar current limits

❌ Required for DP

You must add:

- Positive and negative sequence voltage measurement

- PLL response to unbalanced voltages

- Separate I1and I2current control (or explicit rejection)

- Phase-dependent current limits

- Sequence-aware fault ride-through logic

Important:
These states do not exist in traditional +seq inverter models. They must be added.

2. What Must Happen to Positive-Sequence Dynamic Models for DP to Use Them?

This is the critical question. DP is not just +seq RMS with more inputs. Models must be structurally transformed.

A. Network Models: Lift the Balance Constraint

What Must Change

- Replace the single algebraic voltage equation with:

  - Three phase equations or

  - Coupled V1, V2, V0equations

- Allow sequence-coupling through network elements

Practical Implication

- Existing +seq Y-bus cannot be reused

- A multi-sequence or phase Y-bus must be constructed

B. Generator & Motor Models: Replicate and Couple Sequences

Required Transformation

- Duplicate machine electrical equations for:

  - Positive sequence

  - Negative sequence

- Couple them through:

  - Electromagnetic torque

  - Mechanical dynamics

What Stays the Same

- Governor dynamics

- Exciter outer loops

What Changes

- Electrical torque now contains:

Te=Te1+Te2

+seq models omit Te2entirely.

C. Inverter Models: From dq-Only to Sequence-Aware Control

This cannot be automated.

Required Structural Changes

- PLL must operate on unbalanced phasors

- dq transforms must be sequence-selective

- Controllers must accept oscillatory inputs (2ω content)

- Limiters must act per phase or per sequence

Key Point

A positive-sequence inverter model cannot be “wrapped” into DP.
It must be re-formulated.

D. Load Models: Scalar → Vector

Required Changes

- Replace scalar voltage dependency with:

  - Phase-wise voltage

  - Or sequence-wise voltage

- Enable redistribution of power during unbalance

E. Initialization: From +Seq Power Flow → 3-Phase PF

What Must Change

- DP requires:

  - Va,Vb,Vc(or V1,V2,V0) initial values

- Positive-sequence power flow is insufficient

- A 3-phase unbalanced PF must be solved first

3. Why This Is Not Just a Data Problem (But a Modeling One)

Summary of the core issue:

| Aspect | +Seq RMS | DP |
| --- | --- | --- |
| Network | Balanced | Unbalanced |
| Controls | Scalar & dq | Sequence-coupled |
| Dynamics | Averaged | Oscillatory allowed |
| Physics | Assumed symmetry | Symmetry broken |

Positive-sequence programs intentionally delete degrees of freedom that DP needs. They are not “missing fields” — they are missing states and equations.

Final Bottom Line

Additional data DP needs that +seq programs do not have:

- Z2,Z0, phase coupling

- Grounding topology

- Phase-resolved loads

- Sequence-aware inverter control parameters

- Negative-sequence machine dynamics

- 3-phase power flow initialization

What must happen to +seq dynamics to use DP:

- Balanced assumptions must be removed

- States must be duplicated per sequence or phase

- Control equations must explicitly handle unbalance

- Many inverter models must be re-written, not converted

One-sentence takeaway

Dynamic Phasors are not an extension of positive-sequence dynamics — they are a fundamentally higher-order model that requires new states, new equations, and new initialization, not just additional data.

If you want, next I can:

- Show exactly which PSS®E/PowerWorld dynamic model parameters survive DP

- Sketch a model-conversion decision tree (what can be reused vs rewritten)

- Map this to DPsim, PowerFactory DP, or PSCAD-RMS

Just tell me which environment you care about.